## Heat Generators
| name | installed capacity (MW_th) | efficiency th | efficiency el | investment costs (MSEK/MW_th) | OPEX fix (SEK/MW_th) | OPEX var (EUR/MWh) | Coldstart Costs (EUR/Start) | life time | renewable factor | must run [0-1] | Maximal Available Potential [MWh] | Maximal Output Power [MW] | Excess Heat Source Price [EUR/MWh] | Ramping Costs [EUR/MWh] | type | COP source temperature sensitivity (1/°C) | COP flow temperature sensitivity (1/°C) | COP return temperature sensitivity (1/°C) | min shutoff source temperature (°C) | fade out temp where power reduction starts (°C) | Source Temperature (°C) | Nominal Inlet Temperature (°C) | Nominal Return Temperature (°C) | Refrigerants | Maximum Power of the Heatpump Compressor Pel (MW) | Minimum Output Power Factor [0-1] | Electricity price | Sale Electricity price
0 | Waste Incineration CHP |  | 0.86 | 0.26 | See table in sheet -'capital cost table' | See table in sheet -'fixed cost table' | See table in sheet -'variable costs' |  | 26 |  | 0.1 |  |  |  |  | CHP-BP
1 | Electric Boilers |  | 0.98 |  | See table in sheet -'capital cost table' | See table in sheet -'fixed cost table' | See table in sheet -'variable costs' |  | 20 | [6 empty] | boiler | 0.0387 | -0.0159 | -0.0046 | -17 | -2 | 0 | 90 | 35
2 | Sea Water Heat Pumps |  | 2.68 |  | See table in sheet -'capital cost table' | See table in sheet -'fixed cost table' | See table in sheet -'variable costs' |  | 20 | [6 empty] | Heat Pump Seawater | 0.0578 | -0.0247 | -0.0136 | -1 | 6 | 4 | 80 | 40
3 | Bio Pellets CHP |  | 0.7 | 0.21 | See table in sheet -'capital cost table' | See table in sheet -'fixed cost table' | See table in sheet -'variable costs' |  | 28 | [6 empty] | CHP-BP
4 | Wood Chips CHP |  | 0.8 | 0.27 | See table in sheet -'capital cost table' | See table in sheet -'fixed cost table' | See table in sheet -'variable costs' |  | 28 | [6 empty] | CHP-BP
5 | Bio Oil HOBs |  | 0.9 |  | See table in sheet -'capital cost table' | See table in sheet -'fixed cost table' | See table in sheet -'variable costs' |  | 20 | [6 empty] | boiler
6 | Bio Oil CHP |  | 0.8 | 0.5 | See table in sheet -'capital cost table' | See table in sheet -'fixed cost table' | See table in sheet -'variable costs' |  | 20 | [6 empty] | CHP-BP
7 | Data Centre Heat Pumps |  | 3.2 | [5 empty] | 20 | [6 empty] | Heat Pump Data Center | 0.0578 | -0.0247 | -0.0136 | 3 | 6 | 4 | 80 | 40
8 | Sewage Treatment Heat Pumps |  | 2.8 | [5 empty] | 20 | [6 empty] | Heat Pump Wastewater | 0.0578 | -0.0247 | -0.0136 | 3 | 6 | 4 | 80 | 40
9 | Low Temperature Sources Heat Pumps |  | 2.7 | [5 empty] | 20 | [6 empty] | Heat Pump River Water | 0.0578 | -0.0247 | -0.0136 | 3 | 6 | 4 | 80 | 40

## Maximal Available Potential
Technology/Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Bio Oil HOBs | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3 | 2494782.3
Bio Pellets CHP | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000
Waste Incineration CHP | 7692561.54 | 7692561.54 | 7692561.54 | 7416809.334 | 7146557.172 | 6881555.052 | 6621802.974 | 6366800.934 | 6117048.936 | 5872046.976 | 5632045.056 | 5396543.172 | 5166041.328 | 4940039.52 | 4773288.186 | 4609786.878 | 4449535.596 | 4292284.338 | 4138033.104 | 3986781.894 | 3838530.708 | 3693029.544 | 3550778.406 | 3410777.286 | 3273776.19 | 3139525.116 | 3008024.064 | 2878773.03 | 2803772.43
Bio Oil CHP | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34 | 2872592.34
Electric Boilers | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82 | 3057848.82
Sea Water Heat Pumps | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92 | 5973154.92
Wood Chips CHP | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56 | 7738855.56
Data Centre Heat Pumps
Sewage Treatment Heat Pumps
Low Temperature Sources Heat Pumps
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unit: MSEK/MW

## installed capacities
name | Temperature | Price | 2023 | 2030 | 2035 | 2040 | 2045 | 2050
Waste Incineration CHP | Low | Low | 354 | 526.6707 | 492.6707 | 366.6707 | 294.0946 | 248.6013
Electric Boilers | Low | Low | 430 | 129 | 125.2193 | 209.7832 | 320.0628 | 320.0628
Sea Water Heat Pumps | Low | Low | 320 | 243 | 10.6436 | 321.1862 | 766.376 | 766.376
Bio Pellets CHP | Low | Low | 185 | 185 | 93 | 0 | 0 | 0
Wood Chips CHP | Low | Low | 522 | 490 | 425 | 414 | 233.7454 | 319.9328
Bio Oil HOBs | Low | Low | 1714 | 1540 | 1114.2005 | 1151.3075 | 1207.618 | 1223.8361
Bio Oil CHP | Low | Low | 275 | 83 | 0 | 0 | 0 | 0
Data Centre Heat Pumps | Low | Low | 0 | 200 | 575.5382 | 575.5382 | 575.5382 | 575.5382
Sewage Treatment Heat Pumps | Low | Low | 220 | 250 | 250 | 250 | 250 | 250
Low Temperature Sources Heat Pumps | Low | Low | 0 | 0 | 5.9003 | 18.0902 | 76.1405 | 76.1405
Waste Incineration CHP | Low | High | 354 | 490.4081 | 456.4081 | 330.4081 | 276.4559 | 258.5939
Electric Boilers | Low | High | 430 | 129 | 126.1349 | 400 | 400 | 400
Sea Water Heat Pumps | Low | High | 320 | 243.2 | 38.36 | 78.5436 | 251.8715 | 319.5616
Bio Pellets CHP | Low | High | 185 | 185 | 93 | 0 | 0 | 0
Wood Chips CHP | Low | High | 522 | 490 | 508.516 | 814 | 900 | 900
Bio Oil HOBs | Low | High | 1714 | 1540 | 783 | 428.6613 | 415.1079 | 426.0836
Bio Oil CHP | Low | High | 275 | 83 | 0 | 0 | 0 | 0
Data Centre Heat Pumps | Low | High | 0 | 200 | 532.5601 | 532.5601 | 532.5601 | 532.5601
Sewage Treatment Heat Pumps | Low | High | 220 | 250 | 250 | 250 | 250 | 250
Low Temperature Sources Heat Pumps | Low | High | 0 | 0 | 0.27905 | 0.27905 | 0.27905 | 0.59865
Waste Incineration CHP | High | Low | 354 | 523.1338 | 489.1338 | 363.1338 | 285.1913 | 259.8045
Electric Boilers | High | Low | 430 | 129 | 11.2868 | 239.7601 | 389.6596 | 389.6596
Sea Water Heat Pumps | High | Low | 320 | 243 | 243.3333 | 320 | 498.8851 | 576.8851
Bio Pellets CHP | High | Low | 185 | 185 | 93 | 0 | 0 | 0
Wood Chips CHP | High | Low | 522 | 490 | 425 | 414 | 466.8834 | 441
Bio Oil HOBs | High | Low | 1714 | 1540 | 967.767 | 1159.8737 | 1229.3884 | 1248.3722
Bio Oil CHP | High | Low | 275 | 83 | 0 | 0 | 0 | 0
Data Centre Heat Pumps | High | Low | 0 | 200 | 546.1849 | 571.5315 | 571.5315 | 571.5315
Sewage Treatment Heat Pumps | High | Low | 220 | 250 | 186.8558 | 250 | 250 | 250
Low Temperature Sources Heat Pumps | High | Low | 0 | 0 | 0 | 13.4537 | 32.8534 | 69.7634
Waste Incineration CHP | High | High | 354 | 507.4232 | 473.4232 | 347.4232 | 316.6774 | 315.9209
Electric Boilers | High | High | 430 | 129 | 124.3056 | 400 | 400 | 400
Sea Water Heat Pumps | High | High | 320 | 243 | 10 | 0 | 197.3356 | 247.5221
Bio Pellets CHP | High | High | 185 | 185 | 93 | 0 | 0 | 0
Wood Chips CHP | High | High | 522 | 490 | 546.4033 | 877.2282 | 900 | 900
Bio Oil HOBs | High | High | 1714 | 1540 | 783 | 426.7606 | 426.8858 | 437.2696
Bio Oil CHP | High | High | 275 | 83 | 0 | 0 | 0 | 0
Data Centre Heat Pumps | High | High | 0 | 200 | 530.0487 | 530.0487 | 530.0487 | 530.0487
Sewage Treatment Heat Pumps | High | High | 220 | 247.1931 | 220.3954 | 250 | 250 | 250
Low Temperature Sources Heat Pumps | High | High | 0 | 0 | 0 | 0 | 0 | 0

## capital cost table
Technology/Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Bio Oil HOBs | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.41 | 3.39 | 3.37 | 3.34 | 3.32 | 3.3 | 3.27 | 3.25 | 3.23 | 3.21 | 3.18 | 3.16 | 3.14 | 3.11 | 3.09 | 3.07 | 3.05 | 3.02 | 3 | 2.98
Bio Pellets CHP | 81.41 | 81.41 | 81.07 | 80.72 | 80.38 | 80.04 | 79.69 | 79.35 | 79.01 | 79.01 | 79.01 | 79.01 | 79.01 | 79.01 | 79.01 | 79.01 | 79.01 | 79.01 | 79.01 | 78.78 | 78.55 | 78.32 | 78.09 | 77.86 | 77.63 | 77.4 | 77.17 | 76.94 | 76.72
Waste Incineration CHP | 40.7 | 40.7 | 40.53 | 40.36 | 40.19 | 40.02 | 39.85 | 39.67 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.39 | 39.27 | 39.16 | 39.04 | 38.93 | 38.82 | 38.7 | 38.59 | 38.47 | 38.36
Bio Oil CHP | 22.58 | 22.58 | 22.47 | 22.35 | 22.24 | 22.13 | 22.02 | 21.91 | 21.79 | 21.68 | 21.57 | 21.46 | 21.34 | 21.23 | 21.12 | 21.01 | 20.89 | 20.78 | 20.67 | 20.56 | 20.45 | 20.33 | 20.22 | 20.11 | 20 | 19.88 | 19.77 | 19.66 | 19.66
Electric Boilers | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38
Sea Water Heat Pumps | 7.42 | 7.42 | 7.37 | 7.33 | 7.28 | 7.24 | 7.19 | 7.14 | 7.1 | 7.05 | 7.01 | 6.96 | 6.92 | 6.87 | 6.82 | 6.78 | 6.73 | 6.69 | 6.64 | 6.6 | 6.55 | 6.5 | 6.46 | 6.41 | 6.37 | 6.32 | 6.27 | 6.23 | 6.18
Wood Chips CHP | 41.22 | 41.22 | 40.99 | 40.76 | 40.53 | 40.3 | 40.08 | 39.85 | 39.62 | 39.39 | 39.16 | 38.93 | 38.7 | 38.47 | 38.24 | 38.01 | 37.79 | 37.56 | 37.33 | 37.1 | 36.87 | 36.64 | 36.41 | 36.18 | 35.95 | 35.72 | 35.5 | 35.27 | 35.04
Data Centre Heat Pumps | 7.42 | 7.42 | 7.37 | 7.33 | 7.28 | 7.24 | 7.19 | 7.14 | 7.1 | 7.05 | 7.01 | 6.96 | 6.92 | 6.87 | 6.82 | 6.78 | 6.73 | 6.69 | 6.64 | 6.6 | 6.55 | 6.5 | 6.46 | 6.41 | 6.37 | 6.32 | 6.27 | 6.23 | 6.18
Sewage Treatment Heat Pumps | 7.42 | 7.42 | 7.37 | 7.33 | 7.28 | 7.24 | 7.19 | 7.14 | 7.1 | 7.05 | 7.01 | 6.96 | 6.92 | 6.87 | 6.82 | 6.78 | 6.73 | 6.69 | 6.64 | 6.6 | 6.55 | 6.5 | 6.46 | 6.41 | 6.37 | 6.32 | 6.27 | 6.23 | 6.18
Low Temperature Sources Heat Pumps | 10.42 | 10.42 | 10.37 | 10.33 | 10.28 | 10.24 | 10.19 | 10.14 | 10.1 | 10.05 | 10.01 | 9.96 | 9.92 | 9.87 | 9.82 | 9.78 | 9.73 | 9.69 | 9.64 | 9.6 | 9.55 | 9.5 | 9.46 | 9.41 | 9.37 | 9.32 | 9.27 | 9.23 | 9.18
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unit: MSEK/MW

## fixed cost table
Technology/Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Bio Oil HOBs | 0.025 | 0.025 | 0.025 | 0.02 | 0.025 | 0.025 | 0.025 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Bio Pellets CHP | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.06
Waste Incineration CHP | 2.26 | 2.26 | 2.25 | 2.24 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.06
Bio Oil CHP | 2.26 | 2.26 | 2.25 | 2.24 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.06
Electric Boilers | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Sea Water Heat Pumps | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02
Wood Chips CHP | 2.245 | 2.245 | 2.24 | 2.235 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.06
Data Centre Heat Pumps | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Sewage Treatment Heat Pumps | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02
Low Temperature Sources Heat Pumps | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unit: MSEK/MW

## variable costs
Technology/Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Bio Oil HOBs | 2.5 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Bio Pellets CHP | 2.23 | 2.23 | 2.23 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.05 | 2.05
Waste Incineration CHP | 2.23 | 2.23 | 2.23 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.05 | 2.05
Bio Oil CHP | 2.23 | 2.23 | 2.23 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.05 | 2.05
Electric Boilers | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sea Water Heat Pumps | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Wood Chips CHP | 2.23 | 2.23 | 2.23 | 2.23 | 2.21 | 2.2 | 2.19 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.16 | 2.15 | 2.14 | 2.13 | 2.11 | 2.1 | 2.09 | 2.07 | 2.06 | 2.05 | 2.05
Data Centre Heat Pumps | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Sewage Treatment Heat Pumps | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Low Temperature Sources Heat Pumps | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unit: SEK/MWh

## Heat Storage
Year | name | Storage Capacity [MWh] | Hourly Stoarge Losses [%] | maximum unloading power [MW] | maximum loading power [MW] | loading efficiency | unloading efficiency | Invesment costs for additional storage capacity [€/MWh] | OPEX fix [€/MWh] | Life Time [a]
2023 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2024 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2025 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2026 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2027 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2028 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2029 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2030 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2031 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2032 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2033 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2034 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2035 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2036 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2037 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2038 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2039 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2040 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2041 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2042 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2043 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2044 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2045 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2046 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2047 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2048 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2049 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30
2050 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30

## prices and emmision factors
| energy carrier | prices(SEK/MWh) | emission factor [tCO2/MWh]
0 | wood chips |  | 0
1 | bio oil |  | 0
2 | fine bio oil |  | 0
3 | waste |  | 0.34735
4 | bio waste |  | 0
5 | electricity |  | See sheet - 'Emission Factor for electricity'
6 | natural gas |  | N/A
7 | Hardcoal |  | N/A
8 | Syntatic gas |  | N/A
9 | Lignite |  | N/A
10 | radiation |  | N/A
11 | excess heat |  | N/A
12 | geothermal heat |  | N/A
13 | biomethane |  | N/A

## Emission Factor for electricity
Year | Emission Factor (Ton/MWh)
2023 | 0.045
2024 | 0.036
2025 | 0.0288
2026 | 0.023
2027 | 0.0184
2028 | 0.0147
2029 | 0.0118
2030 | 0.0094
2031 | 0.0075
2032 | 0.0053
2033 | 0.0037
2034 | 0.0026
2035 | 0.0018
2036 | 0.0013
2037 | 0.0008
2038 | 0.0005
2039 | 0.0002
2040 | 0.0001
2041 | 0
2042 | 0
2043 | 0
2044 | 0
2045 | 0
2046 | 0
2047 | 0
2048 | 0
2049 | 0
2050 | 0

## Fuel Prices
Year | bio oil | wood chips | waste | fine bio oil | bio waste
2023 | 1547.9876 | 233.9981 | -108.9513 | 1778.3858 | 644.3948
2024 | 1573.1874 | 237.5981 | -112.9865 | 1807.1855 | 655.1948
2025 | 1598.3872 | 241.1981 | -117.0218 | 1839.5853 | 665.9947
2026 | 1627.187 | 244.798 | -121.057 | 1871.985 | 676.7946
2027 | 1655.9868 | 248.398 | -125.0922 | 1904.3848 | 687.5945
2028 | 1681.1866 | 251.998 | -129.1275 | 1933.1845 | 698.3944
2029 | 1709.9863 | 259.1979 | -133.1627 | 1969.1842 | 712.7943
2030 | 1738.7861 | 262.7979 | -137.1979 | 2001.584 | 723.5942
2031 | 1771.1858 | 266.3979 | -141.2332 | 2033.9837 | 734.3941
2032 | 1799.9856 | 269.9978 | -145.2684 | 2069.9834 | 748.794
2033 | 1828.7854 | 277.1978 | -149.3036 | 2069.9834 | 759.5939
2034 | 1861.1851 | 280.7978 | -151.9938 | 2105.9832 | 773.9938
2035 | 1893.5849 | 284.3977 | -154.6839 | 2141.9829 | 788.3937
2036 | 1925.9846 | 291.5977 | -157.3741 | 2177.9826 | 799.1936
2037 | 1958.3843 | 295.1976 | -160.0643 | 2213.9823 | 813.5935
2038 | 1990.7841 | 298.7976 | -162.7544 | 2253.582 | 827.9934
2039 | 2026.7838 | 305.9976 | -165.4446 | 2289.5817 | 842.3933
2040 | 2059.1835 | 309.5975 | -168.1347 | 2329.1814 | 856.7931
2041 | 2095.1832 | 316.7975 | -170.8249 | 2368.781 | 871.193
2042 | 2131.183 | 320.3974 | -173.515 | 2408.3807 | 885.5929
2043 | 2167.1827 | 327.5974 | -176.2052 | 2451.5804 | 899.9928
2044 | 2203.1824 | 331.1974 | -178.8953 | 2491.1801 | 914.3927
2045 | 2239.1821 | 338.3973 | -181.5855 | 2534.3797 | 932.3925
2046 | 2278.7818 | 341.9973 | -184.2757 | 2577.5794 | 946.7924
2047 | 2318.3815 | 349.1972 | -186.9658 | 2620.779 | 964.7923
2048 | 2357.9811 | 356.3971 | -189.656 | 2663.9787 | 979.1922
2049 | 2397.5808 | 359.9971 | -195.9882 | 2710.7783 | 997.192
2050 | 2437.1805 | 367.1971 | -199.1589 | 2757.5779 | 1015.1919

## Energy Carrier
| name | carrier
0 | Waste Incineration CHP | waste
1 | Electric Boilers | electricity
2 | Sea Water Heat Pumps | electricity
3 | Bio Pellets CHP | bio waste
4 | Wood Chips CHP | wood chips
5 | Bio Oil HOBs | bio oil
6 | Bio Oil CHP | bio oil
7 | Data Centre Heat Pumps | electricity
8 | Sewage Treatment Heat Pumps | electricity
9 | Low Temperature Sources Heat Pumps | electricity

## Data
| CO2 Price [EUR/tC02] | Interest Rate [0-1] | Minimum Renewable Factor [0-1] | Total Demand[ MWh]
0 | 0 | 0.04 | 0

## co2 price
Year | CO2 price (SEK/tCO2)
2023 | 80
2024 | 90
2025 | 100
2026 | 110
2027 | 120
2028 | 130
2029 | 140
2030 | 150
2031 | 160
2032 | 170
2033 | 180
2034 | 190
2035 | 200
2036 | 210
2037 | 220
2038 | 230
2039 | 240
2040 | 250
2041 | 260
2042 | 270
2043 | 280
2044 | 290
2045 | 300
2046 | 310
2047 | 320
2048 | 330
2049 | 340
2050 | 350

## demand
Year | demand (GWh)
2023 | 7901.9
2024 | 7941.4
2025 | 7981.1
2026 | 8021
2027 | 8061.1
2028 | 8101.4
2029 | 8141.9
2030 | 8182.6
2031 | 8223.6
2032 | 8264.7
2033 | 8306
2034 | 8347.5
2035 | 8389.3
2036 | 8431.2
2037 | 8473.4
2038 | 8515.7
2039 | 8558.3
2040 | 8601.1
2041 | 8644.1
2042 | 8687.3
2043 | 8730.8
2044 | 8774.4
2045 | 8818.3
2046 | 8862.4
2047 | 8906.7
2048 | 8951.2
2049 | 8996
2050 | 9041

## Default - External Data
| Radiation | Temperature | Electricity price | Sale Electricity price | Heat Demand | Inlet Temperature | Return Temperature | River Temperature | Waste Water Temperature | Seawater Temperature
0 | AT-Cluster 1 # 2050 | AT-Cluster 1 # 2050 | AT # 2050 | AT # 2050 | AT-Cluster 1 # 2050 | AT-Cluster 1 # 2050 | AT-Cluster 1 # 2050 | AT # 2050 | standard # 2050