## Heat Generators
Unnamed: 0 | name | installed capacity (MW_th) | efficiency th | efficiency el | investment costs (EUR/MW_th) | OPEX fix (EUR/MWa) | OPEX var (EUR/MWh) | Coldstart Costs (EUR/Start) | life time | renewable factor | must run [0-1] | Maximal Available Potential [MWh] | Maximal Output Power [MW] | Excess Heat Source Price [EUR/MWh] | Ramping Costs [EUR/MWh] | type | COP source temperature sensitivity (1/°C) | COP flow temperature sensitivity (1/°C) | COP return temperature sensitivity (1/°C) | min shutoff source temperature (°C) | fade out temp where power reduction starts (°C) | Source Temperature (°C) | Nominal Inlet Temperature (°C) | Nominal Return Temperature (°C) | Refrigerants | Maximum Power of the Heatpump Compressor Pel (MW) | Minimum Output Power Factor [0-1] | Electricity price | Sale Electricity price
0 | Waste Incineration CHP | 276.4559 | 0.86 | 0.26 | 38930000 | 2110000 | 2.1 |  | 26 |  | 0.1 | 3410777.286 |  |  |  | CHP-BP
1 | Electric Boilers | 400 | 0.98 |  | 1380000 | 10000 | 1 |  | 20 |  |  | 3057848.82 |  |  |  | boiler | 0.0387 | -0.0159 | -0.0046 | -17 | -2 | 0 | 90 | 35
2 | Sea Water Heat Pumps | 251.8715 | 2.68 |  | 6410000 | 30000 | 0.5 |  | 20 |  |  | 5973154.92 |  |  |  | Heat Pump Seawater | 0.0578 | -0.0247 | -0.0136 | -1 | 6 | 4 | 80 | 40
3 | Bio Pellets CHP | 0 | 0.7 | 0.21 | 77860000 | 2110000 | 2.1 |  | 28 |  |  | 150000 |  |  |  | CHP-BP
4 | Wood Chips CHP | 900 | 0.8 | 0.27 | 36180000 | 2110000 | 2.1 |  | 28 |  |  | 7738855.56 |  |  |  | CHP-BP
5 | Bio Oil HOBs | 415.1079 | 0.9 |  | 3090000 | 20000 | 2 |  | 20 |  |  | 2494782.3 |  |  |  | boiler
6 | Bio Oil CHP | 0 | 0.8 | 0.5 | 20110000 | 2110000 | 2.1 |  | 20 |  |  | 2872592.34 |  |  |  | CHP-BP
7 | Data Centre Heat Pumps | 532.5601 | 3.2 |  | 6410000 | 20000 | 0.5 |  | 20 | [6 empty] | Heat Pump Data Center | 0.0578 | -0.0247 | -0.0136 | 3 | 6 | 4 | 80 | 40
8 | Sewage Treatment Heat Pumps | 250 | 2.8 |  | 6410000 | 30000 | 0.5 |  | 20 | [6 empty] | Heat Pump Wastewater | 0.0578 | -0.0247 | -0.0136 | 3 | 6 | 4 | 80 | 40
9 | Low Temperature Sources Heat Pumps | 0.27905 | 2.7 |  | 9410000 | 30000 | 0.5 |  | 20 | [6 empty] | Heat Pump River Water | 0.0578 | -0.0247 | -0.0136 | 3 | 6 | 4 | 80 | 40

## Heat Storage
Unnamed: 0 | name | Storage Capacity [MWh] | Hourly Stoarge Losses [%] | maximum unloading power [MW] | maximum loading power [MW] | loading efficiency | unloading efficiency | Invesment costs for additional storage capacity [€/MWh] | OPEX fix [€/MWh] | Life Time [a]
0 | heat storage | 2000 | 0.00075 | 200 | 200 | 0.98 | 0.98 | 400 | 0 | 30

## prices and emmision factors
Unnamed: 0 | energy carrier | prices(EUR/MWh) | emission factor [tCO2/MWh]
0 | wood chips | 338.3973 | 0
1 | bio oil | 2239.1821 | 0
2 | fine bio oil | 2534.3797 | 0
3 | waste | -181.5855 | 0.34735
4 | bio waste | 932.3925 | 0
5 | electricity |  | 0
6 | natural gas
7 | Hardcoal
8 | Syntatic gas
9 | Lignite
10 | radiation
11 | excess heat
12 | geothermal heat

## Data
Unnamed: 0 | CO2 Price [EUR/tC02] | Interest Rate [0-1] | Minimum Renewable Factor [0-1] | Total Demand[ MWh]
0 | 300 | 0.04 | 0 | 8818300

## Default - External Data
Unnamed: 0 | Radiation | Temperature | Electricity price | Sale Electricity price | Heat Demand | Inlet Temperature | Return Temperature | River Temperature | Waste Water Temperature | Data Center Temperature | Seawater Temperature
0 | default # 2016 | Sthlm # 0 | high # 2045,150f | high # 2045 | Sthlm # 0 | low # 2045 | low # 2045 | supermarket # 0 | Sthlm # 0 | datacenter # 0 | Sthlm # 0

## Energy Carrier
Unnamed: 0 | name | carrier
0 | Waste Incineration CHP | waste
1 | Electric Boilers | electricity
2 | Sea Water Heat Pumps | electricity
3 | Bio Pellets CHP | bio waste
4 | Wood Chips CHP | wood chips
5 | Bio Oil HOBs | bio oil
6 | Bio Oil CHP | bio oil
7 | Data Centre Heat Pumps | electricity
8 | Sewage Treatment Heat Pumps | electricity
9 | Low Temperature Sources Heat Pumps | electricity